## EDE
#Engineering-Data-Exchange - B.I.G.-EU
PROJECT_NAME | Aggregatsbyte 202
VERSION_OF_REFERENCEFILE
TIMESTAMP_OF_LAST_CHANGE
AUTHOR_OF_LAST_CHANGE
VERSION_OF_LAYOUT | 2.3
# keyname | device obj.-instance | object-name | object-type | object-instance | description | present-value-default | min-present-value | max-present-value | settable | supports COV | hi-limit | low-limit | state-text-reference | unit-code | vendor-specific-address | notification-class
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_01_PV | 70087 | 202_55_00_GT01_01_PV | 0 | 1 | Tempgivare GT01:01 |  |  |  | N | Y | 550 | -10 |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_02_PV | 70087 | 202_55_00_GT01_02_PV | 0 | 2 | Tempgivare GT01:02 |  |  |  | N | Y | 550 | -10 |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT15_01_PV | 70087 | 202_55_00_GT15_01_PV | 0 | 3 | Tempgivare GT15:01 |  |  |  | N | Y | 100 | -1 |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_GP03_01_PV | 70087 | 202_55_00_GP03_01_PV | 0 | 4 | Tryckgivare Expantionskärl |  |  |  | N | Y | 1000 | 0 |  | 55
Aggregatsbyte 202_AS202-122_70087_Return temp | 70087 | Return temp | 0 | 5 | Returledningstemperatur |  |  |  | N | Y | 0 | 0 |  | 95
Aggregatsbyte 202_AS202-122_70087_Flow temp | 70087 | Flow temp | 0 | 6 | Framledningstemperatur |  |  |  | N | Y | 0 | 0 |  | 95
Aggregatsbyte 202_AS202-122_70087_Energy | 70087 | Energy | 0 | 7 | Energiförbrukning |  |  |  | N | Y | 0 | 0 |  | 146
Aggregatsbyte 202_AS202-122_70087_Power | 70087 | Power | 0 | 8 | Effekt |  |  |  | N | Y | 0 | 0 |  | 48
Aggregatsbyte 202_AS202-122_70087_Volyme Flow | 70087 | Volyme Flow | 0 | 9 | Flöde |  |  |  | N | Y | 0 | 0 |  | 95
Aggregatsbyte 202_AS202-122_70087_Volyme | 70087 | Volyme | 0 | 10 | Volym |  |  |  | N | Y | 0 | 0 |  | 80
Aggregatsbyte 202_AS202-122_70087_Diff temp | 70087 | Diff temp | 0 | 11 | Differenstemperatur |  |  |  | N | Y | 0 | 0 |  | 63
Aggregatsbyte 202_AS202-122_70087_202_55_00_GP01_01_PV | 70087 | 202_55_00_GP01_01_PV | 0 | 12 | Tryckgivare GP01:01 |  |  |  | N | Y | 1000 | 0 |  | 55
Aggregatsbyte 202_AS202-122_70087_AS202_122_GT04_01_V | 70087 | AS202_122_GT04_01_V | 0 | 13 | Ute Temp. Givare |  |  |  | N | Y | 110 | -40 |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_01_CSP1 | 70087 | 202_55_00_GT01_01_CSP1 | 0 | 14 | Beräknat börvärde sommar |  |  |  | N | Y | 100 | -100 |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_02_CSP1 | 70087 | 202_55_00_GT01_02_CSP1 | 0 | 15 | Beräknat börvärde sommar |  |  |  | N | Y | 100 | -100 |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_01_GT01_01_PV | 70087 | 202_55_01_GT01_01_PV | 0 | 16 | Tempgivare GT01:01 |  |  |  | N | Y | 550 | -10 |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_01_CSP2 | 70087 | 202_55_00_GT01_01_CSP2 | 0 | 17 | Beräknat börvärde sommar |  |  |  | N | Y | 100 | -100 |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_02_CSP2 | 70087 | 202_55_00_GT01_02_CSP2 | 0 | 18 | Beräknat börvärde sommar |  |  |  | N | Y | 100 | -100 |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_01_OP | 70087 | 202_55_00_SV01_01_OP | 0 | 19 | Utsignal |  |  |  | N | Y | 0 | 0 |  | 98
Aggregatsbyte 202_AS202-122_70087_202_55_01_GT15_01_PV | 70087 | 202_55_01_GT15_01_PV | 0 | 20 | Tempgivare GT15:01 |  |  |  | N | Y | 550 | -10 |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_01_CSP | 70087 | 202_55_00_GT01_01_CSP | 0 | 21 | Beräknat börvärde |  |  |  | N | Y | 0 | 0 |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_02_OP | 70087 | 202_55_00_SV01_02_OP | 0 | 22 | Utsignal |  |  |  | N | Y | 0 | 0 |  | 98
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_02_CSP | 70087 | 202_55_00_GT01_02_CSP | 0 | 23 | Beräknat börvärde |  |  |  | N | Y | 0 | 0 |  | 95
Aggregatsbyte 202_AS202-122_70087_Return temp | 70087 | Return temp | 0 | 24 | Returledningstemperatur |  |  |  | N | Y | 0 | 0 |  | 95
Aggregatsbyte 202_AS202-122_70087_Flow temp | 70087 | Flow temp | 0 | 25 | Framledningstemperatur |  |  |  | N | Y | 0 | 0 |  | 95
Aggregatsbyte 202_AS202-122_70087_Energy | 70087 | Energy | 0 | 26 | Energiförbrukning |  |  |  | N | Y | 0 | 0 |  | 146
Aggregatsbyte 202_AS202-122_70087_Power | 70087 | Power | 0 | 27 | Effekt |  |  |  | N | Y | 0 | 0 |  | 48
Aggregatsbyte 202_AS202-122_70087_Volyme Flow | 70087 | Volyme Flow | 0 | 28 | Flöde |  |  |  | N | Y | 0 | 0 |  | 95
Aggregatsbyte 202_AS202-122_70087_Volyme | 70087 | Volyme | 0 | 29 | Volym |  |  |  | N | Y | 0 | 0 |  | 80
Aggregatsbyte 202_AS202-122_70087_Diff temp | 70087 | Diff temp | 0 | 30 | Differenstemperatur |  |  |  | N | Y | 0 | 0 |  | 63
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_01_OP | 70087 | 202_55_00_P02_01_OP | 0 | 31 | Utsignal |  |  |  | N | Y | 0 | 0 |  | 98
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_02_OP | 70087 | 202_55_00_P02_02_OP | 0 | 33 | Utsignal |  |  |  | N | Y | 0 | 0 |  | 98
Aggregatsbyte 202_AS202-122_70087_202_55_01_SV01_02_OP | 70087 | 202_55_01_SV01_02_OP | 0 | 36 | Utsignal |  |  |  | N | Y | 110 | -10 |  | 98
Aggregatsbyte 202_AS202-122_70087_202_55_01_SV01_01_OP | 70087 | 202_55_01_SV01_01_OP | 0 | 37 | Utsignal |  |  |  | N | Y | 110 | -10 |  | 98
Aggregatsbyte 202_AS202-122_70087_202_122_XA01_01_AL_DI | 70087 | 202_122_XA01_01_AL_DI | 3 | 1 | Brandlarm utlöst larmindikering |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_122_XA01_02_AL_DI | 70087 | 202_122_XA01_02_AL_DI | 3 | 2 | Automatsäkring utlöst larmindikering |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_122_XA01_03_AL_DI | 70087 | 202_122_XA01_03_AL_DI | 3 | 3 | Fasavbrott utlöst larmindikering |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_122_XA01_04_DI | 70087 | 202_122_XA01_04_DI | 3 | 4 | Indikering Cirkulationsaggregat |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_122_JFB01_01_AL_DI | 70087 | 202_122_JFB01_01_AL_DI | 3 | 5 | Jordfelsbrytare utlöst larmindikering |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_MH01_01_V | 70087 | 202_55_00_MH01_01_V | 3 | 6 | Serviceomkopplare indikering |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_01_V | 70087 | 202_55_00_P02_01_V | 3 | 7 | Cirkulationspump Driftindikering |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_02_V | 70087 | 202_55_00_P02_02_V | 3 | 8 | Cirkulationspump Driftindikering |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_03_V1 | 70087 | 202_55_00_SV01_03_V1 | 3 | 9 | Indikering Öppet |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_03_V0 | 70087 | 202_55_00_SV01_03_V0 | 3 | 10 | Indikering Stängt |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_04_V1 | 70087 | 202_55_00_SV01_04_V1 | 3 | 11 | Indikering Öppet |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_04_V0 | 70087 | 202_55_00_SV01_04_V0 | 3 | 12 | Indikering Stängt |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_AUTO_V | 70087 | 202_55_00_AUTO_V | 3 | 14 | 202_55_00_AUTO_V |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_STOPP_V | 70087 | 202_55_00_STOPP_V | 3 | 15 | 202_55_00_STOPP_V |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_HAND_V | 70087 | 202_55_00_HAND_V | 3 | 16 | 202_55_00_HAND_V |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_04_AL1 | 70087 | 202_55_00_SV01_04_AL1 | 3 | 21 | Ventil ej Stängd |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_04_AL2 | 70087 | 202_55_00_SV01_04_AL2 | 3 | 22 | Ventil ej Öppen |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_03_AL1 | 70087 | 202_55_00_SV01_03_AL1 | 3 | 23 | Ventil ej Stängd |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_03_AL2 | 70087 | 202_55_00_SV01_03_AL2 | 3 | 24 | Ventil ej Öppen |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_XA01_01_AL | 70087 | XA01_01_AL | 3 | 26 | Brandlarm utlöst |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_XA01_02_AL | 70087 | XA01_02_AL | 3 | 27 | Automatsäkring utlöst |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_01_AL1 | 70087 | 202_55_00_P02_01_AL1 | 3 | 28 | Driftfel P03_01 |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_02_AL1 | 70087 | 202_55_00_P02_02_AL1 | 3 | 29 | Driftfel P03_02 |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_GP03_01_HP_AL | 70087 | 202_55_00_GP03_01_HP_AL | 3 | 30 | Högt tryck exp. |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_MH01_01_AL | 70087 | 202_55_00_MH01_01_AL | 3 | 31 | EJ i Auto |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_AUTO_AL | 70087 | 202_55_00_AUTO_AL | 3 | 32 | Ej i Auto |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_GP03_01_LP_AL | 70087 | 202_55_00_GP03_01_LP_AL | 3 | 33 | lågt tryck exp. |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_02_AL | 70087 | 202_55_00_GT01_02_AL | 3 | 34 | Avvikelselarm |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_01_AL | 70087 | 202_55_00_GT01_01_AL | 3 | 35 | Avvikelselarm |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_01_FAULT | 70087 | 202_55_00_GT01_01_FAULT | 3 | 36 | Givarfelslarm |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_02_FAULT | 70087 | 202_55_00_GT01_02_FAULT | 3 | 37 | Givarfelslarm |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT15_03_FAULT | 70087 | 202_55_00_GT15_03_FAULT | 3 | 38 | Givarfelslarm |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_GP03_01_FAULT | 70087 | 202_55_00_GP03_01_FAULT | 3 | 39 | Givarfelslarm |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_XA01_03_AL | 70087 | XA01_03_AL | 3 | 40 | Fasavbrott utlöst |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_XA01_04_AL | 70087 | XA01_04_AL | 3 | 41 | Indikering Cirkulationsaggregat |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_JFB01_01_AL | 70087 | JFB01_01_AL | 3 | 42 | Jordfelsbrytare utlöst |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_VVX01_01_V | 70087 | 202_55_00_VVX01_01_V | 3 | 43 | Driftindikering |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_VVX01_02_V | 70087 | 202_55_00_VVX01_02_V | 3 | 44 | Driftindikering |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_VVX01_01_AL | 70087 | 202_55_00_VVX01_01_AL | 3 | 45 | Driftfel VVX 01:01 |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_VVX01_02_AL | 70087 | 202_55_00_VVX01_02_AL | 3 | 46 | Driftfel VVX01:02 |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_122_OSP01_01_AL_DI | 70087 | 202_122_OSP01_01_AL_DI | 3 | 49 | Överspänningsskydd utlöst larmindikering |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_01_MH01_01_V | 70087 | 202_55_01_MH01_01_V | 3 | 50 | Serviceomkopplare indikering |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_OSP01_01_AL | 70087 | OSP01_01_AL | 3 | 51 | Överspänningsskydd utlöst |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_01_P03_01_V | 70087 | 202_55_01_P03_01_V | 3 | 52 | Cirkulationspump Driftindikering |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_01_AUTO_V | 70087 | 202_55_01_AUTO_V | 3 | 53 | AUTO |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_DDC01_01_AL | 70087 | DDC01_01_AL | 3 | 54 | Stoppad DDC |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_DDC01_02_AL | 70087 | DDC01_02_AL | 3 | 55 | I/O fel |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_DDC01_03_AL | 70087 | DDC01_03_AL | 3 | 56 | Internt fel |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_DDC01_04_AL | 70087 | DDC01_04_AL | 3 | 57 | Kommunikationsfel |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_DDC01_05_AL | 70087 | DDC01_05_AL | 3 | 58 | Spännings fel |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_01_STOPP_V | 70087 | 202_55_01_STOPP_V | 3 | 59 | STOPP |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_01_HAND_V | 70087 | 202_55_01_HAND_V | 3 | 60 | HAND |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_GP01_01_FAULT | 70087 | 202_55_00_GP01_01_FAULT | 3 | 64 | Givarfelslarm |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_AS202_122_GT04_01_FAULT | 70087 | AS202_122_GT04_01_FAULT | 3 | 65 | Givarfelslarm |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_01_02_AL | 70087 | 202_55_00_P02_01_02_AL | 3 | 66 | Larm P02_01 & P02_02 |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_GP01_01_AL | 70087 | 202_55_00_GP01_01_AL | 3 | 68 | Avvikelselarm |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_01_P03_01_AL1 | 70087 | 202_55_01_P03_01_AL1 | 3 | 70 | Driftfel P03_01 |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_01_GT01_01_FAULT | 70087 | 202_55_01_GT01_01_FAULT | 3 | 71 | Givarfelslarm |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_01_GT15_01_FAULT | 70087 | 202_55_01_GT15_01_FAULT | 3 | 72 | Givarfelslarm |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_01_GT01_01_AL | 70087 | 202_55_01_GT01_01_AL | 3 | 73 | Avvikelselarm |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_01_MH01_01_AL | 70087 | 202_55_01_MH01_01_AL | 3 | 75 | EJ i Auto |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_01_AUTO_AL | 70087 | 202_55_01_AUTO_AL | 3 | 76 | Ej i Auto |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_01_SP1 | 70087 | 202_55_00_P02_01_SP1 | 2 | 1 | Startfördröjning vid fel | 5 | 0 | 0 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_03_AD1 | 70087 | 202_55_00_SV01_03_AD1 | 2 | 2 | Larmfördröjning | 0,5 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_03_AD2 | 70087 | 202_55_00_SV01_03_AD2 | 2 | 3 | Larmfördröjning | 0,5 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_04_AD1 | 70087 | 202_55_00_SV01_04_AD1 | 2 | 4 | Larmfördröjning | 0,5 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_04_AD2 | 70087 | 202_55_00_SV01_04_AD2 | 2 | 5 | Larmfördröjning | 0,5 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_01_AD1 | 70087 | 202_55_00_P02_01_AD1 | 2 | 6 | Larmfördröjning | 0,5 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_02_AD1 | 70087 | 202_55_00_P02_02_AD1 | 2 | 7 | Larmfördröjning | 0,5 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_MH01_01_AD | 70087 | 202_55_00_MH01_01_AD | 2 | 8 | Larmfördröjning givarfelslarm | 60 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_AUTO_AD | 70087 | 202_55_00_AUTO_AD | 2 | 9 | Larmfördröjning givarfelslarm | 60 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_GP03_01_AD2 | 70087 | 202_55_00_GP03_01_AD2 | 2 | 10 | Larmfördröjning | 30 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_GP03_01_AD3 | 70087 | 202_55_00_GP03_01_AD3 | 2 | 11 | Larmfördröjning | 30 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_GP03_01_SP1 | 70087 | 202_55_00_GP03_01_SP1 | 2 | 12 | lågt tryck exp. | 1 | 0 | 0 | Y | Y |  |  |  | 55
Aggregatsbyte 202_AS202-122_70087_202_55_00_GP03_01_SP2 | 70087 | 202_55_00_GP03_01_SP2 | 2 | 13 | Högt tryck exp. | 2,4 | 0 | 0 | Y | Y |  |  |  | 55
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_02_ADL | 70087 | 202_55_00_GT01_02_ADL | 2 | 14 | Tempavvikelsegräns | 3 | 0 | 0 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_02_AD2 | 70087 | 202_55_00_GT01_02_AD2 | 2 | 15 | Larmfördröjning | 30 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_01_ADL | 70087 | 202_55_00_GT01_01_ADL | 2 | 16 | Tempavvikelsegräns | 3 | 0 | 0 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_01_AD2 | 70087 | 202_55_00_GT01_01_AD2 | 2 | 17 | Larmfördröjning | 30 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_01_AD1 | 70087 | 202_55_00_GT01_01_AD1 | 2 | 18 | Larmfördröjning | 30 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_02_AD1 | 70087 | 202_55_00_GT01_02_AD1 | 2 | 19 | Larmfördröjning | 30 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT15_03_AD1 | 70087 | 202_55_00_GT15_03_AD1 | 2 | 20 | Larmfördröjning | 30 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_GP03_01_AD1 | 70087 | 202_55_00_GP03_01_AD1 | 2 | 21 | Larmfördröjning | 30 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_02_SP1 | 70087 | 202_55_00_P02_02_SP1 | 2 | 22 | Startfördröjning vid fel | 5 | 0 | 0 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_VX_SP1 | 70087 | 202_55_00_VX_SP1 | 2 | 23 | Stoppfördröjning vid växling | 30 | 0 | 0 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_VVX_SP1 | 70087 | 202_55_00_VVX_SP1 | 2 | 24 | Stoppfördröjning vid växling | 0 | 0 | 0 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_VVX1_SP1 | 70087 | 202_55_00_VVX1_SP1 | 2 | 25 | Start sterg 2 | 4 | 0 | 0 | Y | Y |  |  |  | 87
Aggregatsbyte 202_AS202-122_70087_202_55_00_VVX2_SP1 | 70087 | 202_55_00_VVX2_SP1 | 2 | 26 | Start steg 1 | 5 | 0 | 0 | Y | Y |  |  |  | 87
Aggregatsbyte 202_AS202-122_70087_XA01_01_AD | 70087 | XA01_01_AD | 2 | 28 | Larmfördröjning Brandlarm utlöst | 1 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_S_GT01_01_X1 | 70087 | 202_55_00_S_GT01_01_X1 | 2 | 29 | Kurva Primärkyla framledning X1 | 6 | -40 | 50 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_S_GT01_01_X2 | 70087 | 202_55_00_S_GT01_01_X2 | 2 | 30 | Kurva Primärkyla framledning X2 | 7 | -40 | 50 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_S_GT01_01_X3 | 70087 | 202_55_00_S_GT01_01_X3 | 2 | 31 | Kurva Primärkyla framledning X3 | 9 | -40 | 50 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_S_GT01_01_X4 | 70087 | 202_55_00_S_GT01_01_X4 | 2 | 32 | Kurva Primärkyla framledning X4 | 11 | -40 | 50 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_S_GT01_01_X5 | 70087 | 202_55_00_S_GT01_01_X5 | 2 | 33 | Kurva Primärkyla framledning X5 | 13 | -40 | 50 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_S_GT01_01_Y5 | 70087 | 202_55_00_S_GT01_01_Y5 | 2 | 34 | Kurva framledningstemp vid Y5 | 15 | 0 | 100 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_S_GT01_01_Y4 | 70087 | 202_55_00_S_GT01_01_Y4 | 2 | 35 | Kurva framledningstemp vid Y4 | 13 | 0 | 100 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_S_GT01_01_Y3 | 70087 | 202_55_00_S_GT01_01_Y3 | 2 | 36 | Kurva framledningstemp vid Y3 | 10 | 0 | 100 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_S_GT01_01_Y2 | 70087 | 202_55_00_S_GT01_01_Y2 | 2 | 37 | Kurva framledningstemp vid Y2 | 8 | 0 | 100 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_S_GT01_01_Y1 | 70087 | 202_55_00_S_GT01_01_Y1 | 2 | 38 | Kurva framledningstemp vid Y1 | 8 | 0 | 100 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_V_GT01_01_X1 | 70087 | 202_55_00_V_GT01_01_X1 | 2 | 39 | Kurva Primärkyla framledning X1 | 6 | -40 | 50 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_V_GT01_01_X2 | 70087 | 202_55_00_V_GT01_01_X2 | 2 | 40 | Kurva Primärkyla framledning X2 | 7 | -40 | 50 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_V_GT01_01_X3 | 70087 | 202_55_00_V_GT01_01_X3 | 2 | 41 | Kurva Primärkyla framledning X3 | 9 | -40 | 50 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_V_GT01_01_X4 | 70087 | 202_55_00_V_GT01_01_X4 | 2 | 42 | Kurva Primärkyla framledning X4 | 11 | -40 | 50 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_V_GT01_01_X5 | 70087 | 202_55_00_V_GT01_01_X5 | 2 | 43 | Kurva Primärkyla framledning X5 | 13 | -40 | 50 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_V_GT01_01_Y5 | 70087 | 202_55_00_V_GT01_01_Y5 | 2 | 44 | Kurva framledningstemp vid Y5 | 15 | 0 | 100 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_V_GT01_01_Y4 | 70087 | 202_55_00_V_GT01_01_Y4 | 2 | 45 | Kurva framledningstemp vid Y4 | 13 | 0 | 100 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_V_GT01_01_Y3 | 70087 | 202_55_00_V_GT01_01_Y3 | 2 | 46 | Kurva framledningstemp vid Y3 | 12 | 0 | 100 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_V_GT01_01_Y2 | 70087 | 202_55_00_V_GT01_01_Y2 | 2 | 47 | Kurva framledningstemp vid Y2 | 11 | 0 | 100 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_V_GT01_01_Y1 | 70087 | 202_55_00_V_GT01_01_Y1 | 2 | 48 | Kurva framledningstemp vid Y1 | 10 | 0 | 100 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_01_P | 70087 | 202_55_00_GT01_01_P | 2 | 49 | Regulator Förstärkning | -0,8 | 0 | 0 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_01_I | 70087 | 202_55_00_GT01_01_I | 2 | 50 | Regulator I-Tid | 2 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_01_OPM | 70087 | 202_55_00_SV01_01_OPM | 2 | 51 | manuell utsignal | 0 | 0 | 0 | Y | Y |  |  |  | 98
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_02_P | 70087 | 202_55_00_GT01_02_P | 2 | 52 | Regulator Förstärkning | -0,8 | 0 | 0 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_02_I | 70087 | 202_55_00_GT01_02_I | 2 | 53 | Regulator I-Tid | 2 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_02_OPM | 70087 | 202_55_00_SV01_02_OPM | 2 | 54 | manuell utsignal | 0 | 0 | 0 | Y | Y |  |  |  | 98
Aggregatsbyte 202_AS202-122_70087_XA01_02_AD | 70087 | XA01_02_AD | 2 | 55 | Larmfördröjning Automatsäkring utlöst | 1 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_XA01_03_AD | 70087 | XA01_03_AD | 2 | 56 | Larmfördröjning Fasavbrott utlöst | 1 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_XA01_04_AD | 70087 | XA01_04_AD | 2 | 57 | Larmfördröjning Indikering Cirkulationsaggregat | 1 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_JFB01_01_AD | 70087 | JFB01_01_AD | 2 | 58 | Larmfördröjning Jordfelsbrytare utlöst | 1 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_VVX01_01_AD | 70087 | 202_55_00_VVX01_01_AD | 2 | 59 | Larmfördröjning | 0,5 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_VVX01_02_AD | 70087 | 202_55_00_VVX01_02_AD | 2 | 60 | Larmfördröjning | 0,5 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_DDC01_01_AD | 70087 | DDC01_01_AD | 2 | 61 | Larmfördröjning Stoppad DDC | 1 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_DDC01_02_AD | 70087 | DDC01_02_AD | 2 | 62 | Larmfördröjning I/O fel | 1 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_DDC01_03_AD | 70087 | DDC01_03_AD | 2 | 63 | Larmfördröjning Internt fel | 1 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_DDC01_04_AD | 70087 | DDC01_04_AD | 2 | 64 | Larmfördröjning Kommunikationsfel | 1 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_DDC01_05_AD | 70087 | DDC01_05_AD | 2 | 65 | Larmfördröjning Spännings fel | 1 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_OSP01_01_AD | 70087 | OSP01_01_AD | 2 | 66 | Larmfördröjning Överspänningsskydd utlöst | 1 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_01_P03_01_SP1 | 70087 | 202_55_01_P03_01_SP1 | 2 | 67 | Stoppfördröjning | 5 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_GP01_01_P | 70087 | 202_55_00_GP01_01_P | 2 | 68 | Regulator Förstärkning | -0,8 | 0 | 0 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_GP01_01_I | 70087 | 202_55_00_GP01_01_I | 2 | 69 | Regulator I-Tid | 2 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_01_OPM | 70087 | 202_55_00_P02_01_OPM | 2 | 70 | manuell utsignal | 0 | 0 | 0 | Y | Y |  |  |  | 98
Aggregatsbyte 202_AS202-122_70087_202_55_00_GP01_01_P | 70087 | 202_55_00_GP01_01_P | 2 | 71 | Regulator Förstärkning | -0,8 | 0 | 0 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_00_GP01_01_I | 70087 | 202_55_00_GP01_01_I | 2 | 72 | Regulator I-Tid | 2 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_02_OPM | 70087 | 202_55_00_P02_02_OPM | 2 | 73 | manuell utsignal | 0 | 0 | 0 | Y | Y |  |  |  | 98
Aggregatsbyte 202_AS202-122_70087_202_55_00_GP01_01_SP | 70087 | 202_55_00_GP01_01_SP | 2 | 74 | Tryck Börvärde | 80 | 0 | 0 | Y | Y |  |  |  | 54
Aggregatsbyte 202_AS202-122_70087_202_55_00_GP01_01_AD1 | 70087 | 202_55_00_GP01_01_AD1 | 2 | 75 | Larmfördröjning | 30 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_AS202-122_GT04_01_AD | 70087 | AS202-122_GT04_01_AD | 2 | 76 | Larmfördröjning | 30 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_01_AD2 | 70087 | 202_55_00_P02_01_AD2 | 2 | 77 | Larmfördröjning | 0,5 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_GP01_01_ADL | 70087 | 202_55_00_GP01_01_ADL | 2 | 79 | Tryckavvikelsegräns | 3 | 0 | 0 | Y | Y |  |  |  | 53
Aggregatsbyte 202_AS202-122_70087_202_55_00_GP01_01_AD2 | 70087 | 202_55_00_GP01_01_AD2 | 2 | 80 | Larmfördröjning | 30 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_01_GT01_01_P | 70087 | 202_55_01_GT01_01_P | 2 | 81 | Förstärkning | -2 | 0 | 0 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_01_GT01_01_I | 70087 | 202_55_01_GT01_01_I | 2 | 82 | I-Tid | 4 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_01_GT01_01_SP | 70087 | 202_55_01_GT01_01_SP | 2 | 83 | Börvärde GT01:01 | 14 | 0 | 0 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_01_SV01_02_OP_OPM | 70087 | 202_55_01_SV01_02_OP_OPM | 2 | 84 | Handläge | 0 | 0 | 100 | Y | Y |  |  |  | 98
Aggregatsbyte 202_AS202-122_70087_202_55_01_SV01_01_OP_OPM | 70087 | 202_55_01_SV01_01_OP_OPM | 2 | 85 | Handläge | 0 | 0 | 100 | Y | Y |  |  |  | 98
Aggregatsbyte 202_AS202-122_70087_202_55_01_P03_01_AD1 | 70087 | 202_55_01_P03_01_AD1 | 2 | 86 | Larmfördröjning | 1 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_01_GT01_01_AD1 | 70087 | 202_55_01_GT01_01_AD1 | 2 | 87 | Larmfördröjning | 60 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_01_GT15_01_AD1 | 70087 | 202_55_01_GT15_01_AD1 | 2 | 88 | Larmfördröjning | 60 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_01_GT01_01_ADL | 70087 | 202_55_01_GT01_01_ADL | 2 | 89 | Tempavvikelsegräns | 3 | 0 | 0 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_01_GT01_01_AD2 | 70087 | 202_55_01_GT01_01_AD2 | 2 | 90 | Larmfördröjning | 30 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_AS202_122_GT04_01_SP | 70087 | AS202_122_GT04_01_SP | 2 | 91 | Larm Blockerings gräns | 15 | 0 | 0 | Y | Y |  |  |  | 95
Aggregatsbyte 202_AS202-122_70087_202_55_01_MH01_01_AD | 70087 | 202_55_01_MH01_01_AD | 2 | 92 | Larmfördröjning givarfelslarm | 60 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_01_AUTO_AD | 70087 | 202_55_01_AUTO_AD | 2 | 93 | Larmfördröjning givarfelslarm | 60 | 0 | 0 | Y | Y |  |  |  | 72
Aggregatsbyte 202_AS202-122_70087_202_55_00_M | 70087 | 202_55_00_M | 5 | 1 | Manuell styrning | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_MCMD | 70087 | 202_55_00_MCMD | 5 | 2 | Manuell utsignal | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_01_M | 70087 | 202_55_00_P02_01_M | 5 | 3 | Manuell styrning | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_01_MCMD | 70087 | 202_55_00_P02_01_MCMD | 5 | 4 | Handläge | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_02_M | 70087 | 202_55_00_P02_02_M | 5 | 8 | Manuell styrning | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_02_MCMD | 70087 | 202_55_00_P02_02_MCMD | 5 | 9 | Handläge | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_VX_MCMD | 70087 | 202_55_00_VX_MCMD | 5 | 10 | Manuell pumpväxling | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_01_V3 | 70087 | 202_55_00_P02_01_V3 | 5 | 11 | Drift P01:01 | 1 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_02_V3 | 70087 | 202_55_00_P02_02_V3 | 5 | 12 | Drift P01:02 | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_VVX_MCMD | 70087 | 202_55_00_VVX_MCMD | 5 | 13 | Manuell VVX växling | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_VVX01_01_V3 | 70087 | 202_55_00_VVX01_01_V3 | 5 | 14 | Drift VVX01_01 | 1 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_VVX01_02_V3 | 70087 | 202_55_00_VVX01_02_V3 | 5 | 15 | Drift VVX01_02 | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_VVX2_MCMD | 70087 | 202_55_00_VVX2_MCMD | 5 | 16 | Start av steg 2 VVX2 | 1 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_VVX1_MCMD | 70087 | 202_55_00_VVX1_MCMD | 5 | 17 | Start av steg 2 VVX1 | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_SOMMAR=1 | 70087 | SOMMAR=1 | 5 | 18 | SOMMAR=1 | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_01_M | 70087 | 202_55_00_SV01_01_M | 5 | 23 | Manuell styrning | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_03_M | 70087 | 202_55_00_SV01_03_M | 5 | 24 | Manuell styrning | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_03_MCMD | 70087 | 202_55_00_SV01_03_MCMD | 5 | 25 | Handläge | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_02_M | 70087 | 202_55_00_SV01_02_M | 5 | 30 | Manuell styrning | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_04_M | 70087 | 202_55_00_SV01_04_M | 5 | 31 | Manuell styrning | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_04_MCMD | 70087 | 202_55_00_SV01_04_MCMD | 5 | 32 | Handläge | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_01_M | 70087 | 202_55_01_M | 5 | 33 | Manuell styrning | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_01_MCMD | 70087 | 202_55_01_MCMD | 5 | 34 | Manuell utsignal | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_01_P03_01_M | 70087 | 202_55_01_P03_01_M | 5 | 35 | Manuell styrning | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_01_P03_01_MCMD | 70087 | 202_55_01_P03_01_MCMD | 5 | 36 | Handläge | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_01_M | 70087 | 202_55_00_P02_01_M | 5 | 37 | Manuell styrning | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_02_M | 70087 | 202_55_00_P02_02_M | 5 | 38 | Manuell styrning | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_01_SV01_02_OP_M | 70087 | 202_55_01_SV01_02_OP_M | 5 | 39 | Manuell styrning | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_01_SV01_01_OP_M | 70087 | 202_55_01_SV01_01_OP_M | 5 | 40 | Manuell styrning | 0 |  |  | Y | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_01_CMD | 70087 | 202_55_00_P02_01_CMD | 4 | 1 | Digital utgång |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_02_CMD | 70087 | 202_55_00_P02_02_CMD | 4 | 2 | Digital utgång |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_01_OP | 70087 | 202_55_00_SV01_01_OP | 1 | 3 | Analog utgång |  |  |  | N | Y
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_03_CMD | 70087 | 202_55_00_SV01_03_CMD | 4 | 4 | Digital utgång |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_02_OP | 70087 | 202_55_00_SV01_02_OP | 1 | 5 | Analog utgång |  |  |  | N | Y
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_04_CMD | 70087 | 202_55_00_SV01_04_CMD | 4 | 6 | Digital utgång |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_01_P03_01_CMD | 70087 | 202_55_01_P03_01_CMD | 4 | 7 | Digital utgång |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_01_OP | 70087 | 202_55_00_P02_01_OP | 1 | 8 | Analog utgång |  |  |  | N | Y
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_02_OP | 70087 | 202_55_00_P02_02_OP | 1 | 9 | Analog utgång |  |  |  | N | Y
Aggregatsbyte 202_AS202-122_70087_202_55_01_SV01_02_OP_CMD | 70087 | 202_55_01_SV01_02_OP_CMD | 1 | 10 | Utsignal (intern) |  |  |  | N | Y
Aggregatsbyte 202_AS202-122_70087_202_55_01_SV01_01_OP_CMD | 70087 | 202_55_01_SV01_01_OP_CMD | 1 | 11 | Utsignal (intern) |  |  |  | N | Y
Aggregatsbyte 202_AS202-122_70087_202-55-00 Pumpmotion | 70087 | 202-55-00 Pumpmotion | 17 | 1 | 202-55-00 Pumpmotion |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_VX_V | 70087 | 202_55_00_VX_V | 17 | 2 | 202_55_00_VX_V |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_VVX_V | 70087 | 202_55_00_VVX_V | 17 | 3 | 202_55_00_VVX_V |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_Sommardrift | 70087 | 202_55_00_Sommardrift | 17 | 4 | 202_55_00_Sommardrift |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202-55-01 Pumpmotion | 70087 | 202-55-01 Pumpmotion | 17 | 5 | 202-55-01 Pumpmotion |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_01_PV | 70087 | 202_55_00_GT01_01_PV | 20 | 1 | 202_55_00_GT01_01_PV |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_02_PV | 70087 | 202_55_00_GT01_02_PV | 20 | 2 | 202_55_00_GT01_02_PV |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT15_01_PV | 70087 | 202_55_00_GT15_01_PV | 20 | 3 | 202_55_00_GT15_01_PV |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_GP03_01_PV | 70087 | 202_55_00_GP03_01_PV | 20 | 4 | 202_55_00_GP03_01_PV |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_Return temp | 70087 | Return temp | 20 | 5 | Return temp |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_Flow temp | 70087 | Flow temp | 20 | 6 | Flow temp |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_Energy | 70087 | Energy | 20 | 7 | Energy |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_Power | 70087 | Power | 20 | 8 | Power |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_Volyme Flow | 70087 | Volyme Flow | 20 | 9 | Volyme Flow |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_Volyme | 70087 | Volyme | 20 | 10 | Volyme |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_Diff temp | 70087 | Diff temp | 20 | 11 | Diff temp |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_01_CSP1 | 70087 | 202_55_00_GT01_01_CSP1 | 20 | 12 | 202_55_00_GT01_01_CSP1 |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_02_CSP1 | 70087 | 202_55_00_GT01_02_CSP1 | 20 | 13 | 202_55_00_GT01_02_CSP1 |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_01_CSP2 | 70087 | 202_55_00_GT01_01_CSP2 | 20 | 14 | 202_55_00_GT01_01_CSP2 |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_02_CSP2 | 70087 | 202_55_00_GT01_02_CSP2 | 20 | 15 | 202_55_00_GT01_02_CSP2 |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_01_OP | 70087 | 202_55_00_SV01_01_OP | 20 | 16 | 202_55_00_SV01_01_OP |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_01_CSP | 70087 | 202_55_00_GT01_01_CSP | 20 | 17 | 202_55_00_GT01_01_CSP |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_SV01_02_OP | 70087 | 202_55_00_SV01_02_OP | 20 | 18 | 202_55_00_SV01_02_OP |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_GT01_02_CSP | 70087 | 202_55_00_GT01_02_CSP | 20 | 19 | 202_55_00_GT01_02_CSP |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_GP01_01_PV | 70087 | 202_55_00_GP01_01_PV | 20 | 20 | 202_55_00_GP01_01_PV |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_AS202_122_GT04_01_V | 70087 | AS202_122_GT04_01_V | 20 | 21 | AS202_122_GT04_01_V |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_01_GT01_01_PV | 70087 | 202_55_01_GT01_01_PV | 20 | 22 | 202_55_01_GT01_01_PV |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_01_GT15_01_PV | 70087 | 202_55_01_GT15_01_PV | 20 | 23 | 202_55_01_GT15_01_PV |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_Return temp | 70087 | Return temp | 20 | 26 | Return temp |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_Flow temp | 70087 | Flow temp | 20 | 27 | Flow temp |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_Energy | 70087 | Energy | 20 | 28 | Energy |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_Power | 70087 | Power | 20 | 29 | Power |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_Volyme Flow | 70087 | Volyme Flow | 20 | 30 | Volyme Flow |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_Volyme | 70087 | Volyme | 20 | 31 | Volyme |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_Diff temp | 70087 | Diff temp | 20 | 32 | Diff temp |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_01_OP | 70087 | 202_55_00_P02_01_OP | 20 | 33 | 202_55_00_P02_01_OP |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_00_P02_02_OP | 70087 | 202_55_00_P02_02_OP | 20 | 34 | 202_55_00_P02_02_OP |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_01_SV01_02_OP | 70087 | 202_55_01_SV01_02_OP | 20 | 35 | 202_55_01_SV01_02_OP |  |  |  | N | N
Aggregatsbyte 202_AS202-122_70087_202_55_01_SV01_01_OP | 70087 | 202_55_01_SV01_01_OP | 20 | 36 | 202_55_01_SV01_01_OP |  |  |  | N | N